## Slide 1: DevOps & Cloud Infrastructure SEIS 665 Week 13
Jason Baker
Adjunct Instructor
Graduate Programs in Software
University of St. Thomas
St. Paul, MN

## Slide 2: Agenda
Data center architecture
  Major data center components
  Data center efficiency
  Data center tiers
Future architectures
Final

## Slide 3: What is a data center?
Specialized physical location designed to support computing infrastructure.
NOT THIS
THIS

## Slide 4: Key Attributes
Physical enclosure for greater security.
High grade electrical and heating, venting & cooling (HVAC) systems for greater reliability.
Easy access to mechanical and computing systems for greater maintainability.

## Slide 5: Overall Architecture
DC consists of both internal and external assets.
  It’s not just a building, it’s a property.
Internal (facility)
  Server room: 50%
  Support equipment: 40%
  Miscellaneous: 10%
    Equipment storage
    Setup bench
    NOC
    Employee workspace
External
  Generators, cooling towers, power transformers, parking lot

## Slide 7: DC Key Components
Power system
Climate control system
Network
Security system
Fire detection and suppression
Server room
Network Operations Center (NOC)

## Slide 8: Power System
Power system is critical for IT system reliability.
3 basic parts:
  Distribution: power from utility providers and generators must be distributed to IT equipment.
  Generation: most DCs have the ability to generate their own power using generators (gensets).
  Switching: DC operator must be able to control flow of power in facility.

## Slide 9: Power Distribution
Power utilities supply power to multiple sub-stations forming separate geographical grids.
One or more feeds from substations connect to transformers at data center facility.
Power is connected through switching infrastructure at facility to Power Distribution Units (PDUs) in server room.
PDUs provide power circuits to individual equipment racks.

## Slide 10
Google data center

## Slide 11: Power Generation
DC operators consider self-generated power to be the most reliable power in facility and primary power source.
  Utility power is used even though it is less reliable because it’s cheaper.
Generators are configured in an N+1 configuration.
  N+1 means that one additional generator is installed beyond what is needed to support the DC (failover for redundancy/ maintenance).
Generators usually run on diesel fuel or natural gas.
  Special mix and heating bed required for cold climates
  Onsite storage tank required (thousands of gallons)
  Emergency response refueling contract

## Slide 12
External generator sitting on fuel
bed.
Internal generator – lower risk of weather-related issues.

## Slide 13: Power Switching
Data centers receive power from multiple sources and need a way to switch from one source to another.
Automatic Transfer Switch (ATS) provides power switching
  Problem: switching power isn’t instantaneous
    Generators need time to start up (5-10 seconds)
    Power phases need time to synchronize (3-phase power)
  Solution: ride time power to bridge gap in time between utility failure and self-generated power.

## Slide 14
Automatic Transfer Switches

## Slide 15: Uninterruptable Power Supply (UPS)
A UPS provides ride time power in a data center facility.
Two key types:
  Batteries (traditional)
    Key benefit: provides 5-10 minutes of ride time power
    Batteries are wired in series and strings go bad over time requiring quarterly audits and maintenance
    More cooling and space required to house
    Environmentally unfriendly
  Flywheels
    Cabinet containing steel or carbon fiber wheel spinning at a high rate, usually in a vacuum on magnetic bearings
    Inertia of spinning wheel generates 8-10 seconds of power
    Very low maintenance
    Low physical space and cooling requirements
    Expensive

## Slide 16
Battery Cabinets
Battery racks
(more common at telco installations)

## Slide 17
Vycon Flywheel

## Slide 18
Data Center Power Distribution Diagram

## Slide 19: Climate Control System
All IT equipment generates heat.
  CPUs, hard drives, power supplies, power transformers, batteries
Climate control has two main concerns:
  Regulating both temperature and humidity
  Air flow throughout facility

## Slide 20: Climate Control
IT equipment is designed to operate within a specific temp/humidity zone.
  Traditional: 65-75F (18-24C), Humidity 45-50%
  Modern: 75-85F (24-27C)
  Low humidity may cause electrostatic discharge and high humidity causes condensation/corrosion
Climate is controlled by circulating cooling agent throughout data center.
  Cooling agent (water/glycol) removes heat from air.

## Slide 21: Cooling Loop
Pumping station in facility moves cooling agent through loop.
Heat is removed from loop using a chiller and cooling tower.
Coolant passes through Computer Room Air Conditioning Units (CRACs) located throughout server room.
  CRACs are similar to your home air conditioners.
  Some units also provide humidification.

## Slide 22
Data Center Cooling Loop Diagram

## Slide 23
Data Center Chillers

## Slide 24
Cooling Towers

## Slide 25: Data Center Air Flow
Air flow is one of the biggest concerns in a data center facility.
Heat is generally removed from the air.
  High powered or high density equipment can generate hotspots in a server room (example: virtualization/blade systems).
  Need to replace hot air with cold air.
Two common server room designs:
  Raised-floor facilities
    distribute cool air throughout facility using a sub-floor plenum space and perforated floor tiles
    Most cabling is located below the tiled floor
  Non-raised floor facilities
    Air is distributed via duct work
    Cabling located on cable ladders and trays above equipment cabinets

## Slide 28: Air Flow Challenges
Biggest challenge is heat containment, trying to maintain separation of hot and cold air.
  Mixing air results in decreased cooling performance and higher operating temps.
Solutions:
  Hot aisle/Cold aisle configurations
    Problem: air can spill over aisles
  Chimneys: evacuate hot air from equipment cabinets into ceiling plenum
  Hot aisle/Cold aisle containment
    Uses curtains, plexiglass partitions, enclosures

## Slide 30: Server Room
This is what most people think of as the “data center”.
Server room houses:
  Equipment racks containing IT equipment
  Power distribution units
  CRAC/ air handling units
  UPS systems (sometimes)
The goal is to place as many racks in the server room as feasible
  Total # racks and rack density depends on power and cooling
    Old datacenters: 1-2KVa/rack
    Newer datacenters: 5-20KVa/rack

## Slide 31
Facebook datacenter (Prineville)

## Slide 32
Equipment lift

## Slide 33: Network
Data centers usually have multiple network entry points.
Fiber located in trenches connecting data center to local fiber access points.
Network equipment usually in separate room or cage within data center.
Redundant network infrastructure is common.
Core routers/switches route data to top of rack (TOR) switches in server room.

## Slide 36: Security System
Data center security is oftentimes the #1 concern of its users.
Security is a combination of tools and practices.
Security is focused on three main areas:
  External perimeter of the facility
  Internal facility spaces
  Organizational security practices

## Slide 37: Securing The Perimeter
Property fencing and access gates
Security cameras
Staffed security checkpoint
Locked external access doors with card scanners or biometric readers
Pressure plates on driveways
Metal mesh walls

## Slide 38
Access checkpoint at
Equinix data center

## Slide 39: Internal Security
Security cameras
Security desk
Man trap
Anti-tailgating detection
Motion detectors
Locked equipment cabinets
Biometric readers
Cages

## Slide 40
Data center man trap with biometric palm reader

## Slide 44: Security Practices
Security patrols
Monitored security cameras and recording
Risk management systems
Security certifications
  SOC 1 (SSAE 16), SOC 2, SOC 3
    SOC 2 & 3 audit against actual benchmarks
  ISO 27001
  PCI-DSS (Payment Card Industry Data Security Standard)

## Slide 45: Fire Suppression
Fire is a big concern in a data center due to high density of power and heat.
  Flammable materials strictly prohibited
  Systems unboxed in separate build room
  Box dust can trigger smoke detection systems
Very Early Smoke Detection Apparatus (VESDA) detectors
Gaseous fire suppression/ FM200
Dry pipe sprinkler system

## Slide 46
VESDA Control Unit
Sprinkler head

## Slide 47
FM200 Tanks

## Slide 48: Data Center Efficiency
Data centers are major consumers of power.
  Facilities consume more power than many towns.
Power efficiency of a data center is measured by its Power Utilization Effectiveness (PUE).
PUE = Total facility power/ IT equipment power

## Slide 49: Data Center Efficiency
Best theoretical PUE is 1.0
  Not possible due to power loss in facility
  Average PUE ~ 2.0
  Large cloud data centers < 1.1
PUE decreases as the utilization of a data center increases.
Example: Data center is using 2MW of power and IT equipment is using 1.25MW. What is the PUE?
Answer: PUE = 2MW/ 1.25MW = 1.6

## Slide 50: Data Center Efficiency
Site data center in optimal climate to take advantage of free air cooling.
  Outside air needs to be in the right temperature and humidity range much of the year
LEED Certification: facility conforms to “green” specifications and materials.
Renewable power: solar, wind, geothermal, hydroelectric

## Slide 51: Data Center Tiers
Tier classification system designed by the Uptime Institute
Tier 1: basic data center with dedicated space for IT systems, UPS, cooling equipment
Tier 2
  Some data center components are N+1
  Redundant critical power and cooling equipment
Tier 3
  All major data center components are N+1
  Concurrently maintainable: a redundant delivery path for power and cooling exists to that any component can be serviced without impacting IT operations
Tier 4
  All of the above, systems are fault tolerant and failover is automated

## Slide 52: Data Center Tiers
Data centers must be audited by the Uptime Institute to receive a tier classification.
Classification doesn’t just cover design
  Certification of Design Documents
  Certification of Constructed Facility
  Certification of Operational Sustainability

## Slide 53: Data Center Site Concerns
Extensive studies are done before the location of a future data center is determined
  Power and fiber utility access
  Zoning to operate generators and industrial equipment
  Environmental concerns:
    Earth quake fault line
    Tornado alley
    Flood zone
    Airport flight path

## Slide 54: Future Data Center Architecture
Future DC designs use more exotic power, cooling methods, and form factors.
PODS: portable data centers built into shipping containers.
  Prefabricated with all necessary equipment
  Easily transported and moved
  Simply connect power, cooling, and network

## Slide 55
PODS

## Slide 56: Micro-data centers
Smaller-scale data centers built in modular fashion from PODs.
  Typically unattended facilities in remote locations
  Computing/storage allowance designed to handle certain amount of capacity die off.
  Microsoft Bing Maps data center

## Slide 58: Modular Datacenters
Build a data center shell with all supporting power and cooling equipment.
Place compute and storage containers into the shell.
Replace containers periodically to upgrade capacity.
Microsoft Chicago/ Azure facility

## Slide 60: Facebook Prineville
Innovative cooling system utilizing outside air, filtration, and evaporative spray system.
Facebook started the Open Compute Project to encourage sharing innovative data center and systems designs.
  Large cloud providers build their own equipment

## Slide 62
Microsoft LES eliminates UPS by combining computer power supply and battery

## Slide 63: Homework
No homework this week.
Good luck on the final exam!